## Introduction
Annexure B: TRANSFORMER TEST REQUIREMENTS
Revision |  | 2
Date |  | 2021-06-08
Note | Test requirements for Transmission Power Transformers
These requirements may be ammended for flachberger transformers

## 33kV and below
Annexure B.1 - Transformer Test Requirements for transformers with maximum voltages of 33kV and below
Test No. | Description | Proposed Test Equipment | 2.5MVA | 5MVA
1 | Factory Tests |  | Requirement | Requirement
1.1 | Main test required as per IEC:
1.1.1 | Temperature rise test |  | Type | Type
1.1.3 | Short circuit test |  | Design Calculation Required/ Results of similar units | Design Calculation Required/ Results of similar units
1.1.4 | Lightning impulse test |  | Type | Type
1.1.5 | Switching Impulse test |  | Not Applicable | Not Applicable
| Separate Source Applied Voltage Test (AV) |  | Routine | Routine
1.1.6 | Induced Voltage Withstand (IVW) |  | Routine | Routine
1.1.7 | Induced Overvoltage Test |  | Routine | Routine
1.1.8 | Induced Overvoltage Test with Partial Discharge Measurement |  | Not Required | Not Required
1.1.9 | Line Terminal AC withstand voltage test (LTAC) |  | Not Required | Not Required
1.1.10 | Chopped impulse test |  | Not Required | Not Required
1.1.11 | Accoustic noise level measurement |  | Type | Type
1.1.12 | Overload test |  | Routine | Routine
1.1.13 | Tan Delta (Windings & Bushings) |  | Routine | Routine
1.1.15 | SFRA ( Doble instrument) |  | Routine | Routine
1.2 | Special tests:
1.2.1 | 1 hour over excitation test 1.12 p.u |  | Not Required | Not Required
1.2.2 | Infrared Scanning (to be done at the same time with Temperature rise test in 1.1.1) |  | Type | Type
1.3 | Any other test
1.3.1 | Voltage Ratio/ Polarity/ Phase relation |  | Routine | Routine
1.3.2 | Winding Resistance |  | Routine | Routine
1.3.3 | No-Load Loss & exitation current |  | Routine | Routine
1.3.4 | Load Losses & Impedance Voltage |  | Routine | Routine
1.3.5 | Zero-Sequence Impedance |  | Routine | Routine
1.3.6 | Test on on-load tap changers |  | Routine | Routine
1.3.7 | Winding Hot Spot Temperature rise measurements |  | Not Required | Not Required
1.3.8 | DC Insulation Resistance |  | Routine | Routine
1.3.9 | Operation of all Devices |  | Routine | Routine
1.3.10 | Leak/ pressure test |  | Routine | Routine
1.3.11 | CT Ratio and Polarity Test |  | Routine | Routine
1.3.12 | Core and Frame Insulation Test |  | Routine | Routine
1.3.13 | Measurement of Dissolved Gas |  | Routine | Routine
1.3.14 | Check of external coating/ Paint thickness |  | Routine | Routine

## 66 & 132kV
Annexure B.2 - Transformer Test Requirements for transformers with maximum voltages of 66 and 132kV
Test No. | Description | Proposed Test Equipment | 2.5MVA | 5MVA | 10MVA | 20MVA | 25MVA | 40MVA | 60MVA | Above 60MVA
1 | Factory Tests |  | Requirement | Requirement | Requirement | Requirement | Requirement | Requirement | Requirement | Requirement
1.1 | Main test required as per IEC:
1.1.1 | Temperature rise test |  | Type | Type | Type | Type | Type | Type | Type | Type
1.1.2 | Short circuit test |  | Design Calculation Required/ Results of similar units | Design Calculation Required/ Results of similar units | Design Calculation Required/ Results of similar units | Design Calculation Required/ Results of similar units | Design Calculation Required/ Results of similar units | Design Calculation Required/ Results of similar units | Design Calculation Required/ Results of similar units | Design Calculation Required/ Results of similar units
1.1.3 | Lightning impulse test |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.1.4 | Switching Impulse test |  | Not Required | Not Required | See notes | See notes | See notes | See notes | See notes | See notes
1.1.5 | Separate Source Applied Voltage Test (AV) |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.1.6 | Induced Voltage Withstand (IVW) |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.1.7 | Induced Overvoltage Test |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.1.8 | Induced Overvoltage Test with Partial Discharge Measurement |  | Not Required | Not Required | Routine | Routine | Routine | Routine | Routine | Routine
1.1.9 | Line Terminal AC withstand voltage test (LTAC) |  | Not Required | Not Required | Routine | Routine | Routine | Routine | Routine | Routine
1.1.10 | Chopped impulse test |  | Not Required | Not Required | Not Required | Not Required | Not Required | Not Required | Not Required | Not Required
1.1.11 | Accoustic noise level measurement |  | Type | Type | Type | Type | Type | Type | Type | Type
1.1.12 | Overload test |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.1.13 | Tan Delta (Windings & Bushings) |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.1.15 | SFRA ( Doble instrument) |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.2 | Special tests:
1.2.1 | 1 hour over excitation test 1.12 p.u |  | Not Required | Not Required | Routine | Routine | Routine | Routine | Routine | Routine
1.2.2 | Infrared Scanning (to be done at the same time with Temperature rise test in 1.1.1) |  | Type | Type | Type | Type | Type | Type | Type | Type
1.3 | Any other test
1.3.1 | Voltage Ratio/ Polarity/ Phase relation |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.2 | Winding Resistance |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.3 | No-Load Loss & exitation current |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.4 | Load Losses & Impedance Voltage |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.5 | Zero-Sequence Impedance |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.6 | Test on on-load tap changers |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.7 | Winding Hot Spot Temperature rise measurements |  | Not Required | Not Required | Not Required | Not Required | Not Required | Type | Type | Type
1.3.8 | DC Insulation Resistance |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.9 | Operation of all Devices |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.10 | Leak/ pressure test |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.11 | CT Ratio and Polarity Test |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.12 | Core and Frame Insulation Test |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.13 | Measurement of Dissolved Gas |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
1.3.14 | Check of external coating/ Paint thickness |  | Routine | Routine | Routine | Routine | Routine | Routine | Routine | Routine
Notes | Not Required for 66kV
Special for 132kV

## 220kV and above
Annexure B.3 - Transformer Test Requirements for transformers with maximum voltages of 220kV and above
Test No. | Description | Proposed Test Equipment | 40MVA | 60MVA | Above 60MVA
1 | Factory Tests |  | Requirement | Requirement | Requirement
1.1 | Main test required as per IEC:
1.1.1 | Temperature rise test |  | Type | Type | Type
1.1.2 | Short circuit test |  | Design Calculation Required/ Results of similar units | Design Calculation Required/ Results of similar units | Design Calculation Required/ Results of similar units
1.1.3 | Lightning impulse test (Full wave) |  | Routine | Routine | Routine
1.1.4 | Switching Impulse test |  | Routine | Routine | Routine
1.1.5 | Separate Source Applied Voltage Test (AV) |  | Routine | Routine | Routine
1.1.6 | Induced Voltage Withstand (IVW) |  | Not Applicable | Not Applicable | Not Applicable
1.1.7 | Induced Overvoltage Test |  | Not Required | Not Required | Not Required
1.1.8 | Induced Overvoltage Test with Partial Discharge Measurement (IVPD) |  | Routine | Routine | Routine
1.1.9 | Line Terminal AC withstand voltage test (LTAC) |  | Routine | Routine | Routine
1.1.10 | Chopped impulse test |  | Not Required | Not Required | Not Required
1.1.11 | Accoustic noise level measurement |  | Type | Type | Type
1.1.12 | Overload test |  | Routine | Routine | Routine
1.1.13 | Tan Delta (Windings & Bushings ) |  | Routine | Routine | Routine
1.1.15 | SFRA ( Doble instrument) |  | Routine | Routine | Routine
1.2 | Special tests:
1.2.1 | 1 hour over excitation test 1.12 p.u |  | Routine | Routine | Routine
1.2.2 | Infrared Scanning (to be done at the same time with Temperature rise test in 1.1.1) |  | Type | Type | Type
1.3 | Any other test
1.3.1 | Voltage Ratio/ Polarity/ Phase relation |  | Routine | Routine | Routine
1.3.2 | Winding Resistance |  | Routine | Routine | Routine
1.3.3 | No-Load Loss & exitation current |  | Routine | Routine | Routine
1.3.4 | Load Losses & Impedance Voltage |  | Routine | Routine | Routine
1.3.5 | Zero-Sequence Impedance |  | Routine | Routine | Routine
1.3.6 | Test on on-load tap changers |  | Routine | Routine | Routine
1.3.7 | Winding Hot Spot Temperature rise measurements |  | Type | Type | Type
1.3.8 | DC Insulation Resistance |  | Routine | Routine | Routine
1.3.9 | Operation of all Devices |  | Routine | Routine | Routine
1.3.10 | Leak/ pressure test |  | Routine | Routine | Routine
1.3.11 | CT Ratio and Polarity Test |  | Routine | Routine | Routine
1.3.12 | Core and Frame Insulation Test |  | Routine | Routine | Routine
1.3.13 | Measurement of Dissolved Gas |  | Routine | Routine | Routine
1.3.14 | Check of external coating/ Paint thickness |  | Routine | Routine | Routine